## EPE Community RFP
NMSU RFP
RFI Log - January 16, 2019
# | Question | Response
1 | Can EPE provide a more concrete site boundary? Are all areas within the site survey acceptable or are we limited to the general area shown in Section 8.3. If we are limited to 8.3, can EPE confirm the location of the north boundary. It is hard to evaluate from the google image. | Limited to the area shown in section 8.3 (AREA 3 of the survey in attachment 8.4).
2 | On page 8 of the RFP, it states that Bidder will be responsible to provide the list of site studies listed. We don't notice Hydrology Report listed. Does this mean that it will be provided by EPE? | Contractor must provide all site permits, studies, and reports necessary for the completion of the project.
3 | The specified battery system is called out as AC coupled. Would EPE consider a DC coupled storage system? | AC-coupled is preferred but bidders are allowed to submit an additional DC-coupled option. EPE will review and consider both options.
4 | Regarding major equipment, we identify the list of acceptable manufacturers within section 8.5. However, in section 3.2 of the bid, EPE mentions that All major equipment and components must be tier-one rated and have the minimum experience of 12 months in operation and similar sized deployment. Are these requirements for all major equipment or just the major storage equipment? Further, when EPE references tier 1, does this mean the Bloomberg defined Tier 1 list, or is EPE's definition of Tier 1 the 12 months install/similar deployment? Please clarify? | The requirements are for all major equipment. EPE's definition of Tier 1.
5 | Is EPE open to consider a string inverter solution? We notice section 8.5.6.1 calls out central, but would a centralized configuration of string inverters be a possibility? | AC-coupled is preferred but bidders are allowed to submit an additional DC-coupled option. EPE will review and consider both options.
6 | It appears that the land is publicly accessible, can bidders visit and walk the terrain without the need to schedule with the land owner? | Bidders are allowed to visit the site as long as they send a notice in advance; EPE will then inform the owner.
7 | Is EPE interested in O&M services? | Yes, the proposal must provide detailed O&M information to include costs, scope and schedule of services, guarantees, contract terms, other.
8 | Can EPE provide more detail on the access roads? | Access roads should be cost effective, low maintenance, designed for the project life. Site access must be off of Cholla Rd.
9 | What is the intended application of the storage component? | Peak shaving, solar shifting, curve smoothing.
10 | Can Chint Power Systems be added to the approved inverter list? | Inverters need to comply with all requirements listed in section 8.5.6 Inverters of the RFP.
11 | Can FTC Solar be added to the approved tracker list? | Trackers need to comply with all requirements listed in section 8.5.4 Tracking Systems of the RFP.
12 | Am I correct to assume there will not be a site walk? | As noted in the RFP, the site walk was conducted on January 8. However, bidders are allowed to visit the site as long as they send a notice in advance; EPE will then inform the owner.
13 | Are the MV lines that we will be connecting to the 12.47 kV located just west of the site? | The interconnection voltage is 23.9 kV. The point of interconnection is yet to be determined; most likely along the north side of the project site.
14 | Does EPE have a list of preferred battery suppliers? | No, EPE does not have such list.
15 | Relative to DC Coupled solutions and the system overall, does EPE have any specific inverter oversizing ratios or are you open to what is approved by the inverter manufacturer? | Open to manufacturer and installer recommendations.
16 | AREA 3 - are there any existing easements by separate instrument not shown on the plat where construction may not be allowed? | There are no easements on AREA 3 that would impede construction.
17 | Please verify if a top and bottom rail - 7' galvanized steel chain link fence will be acceptable for perimeter fencing or if an ornamental fence is required? If an ornamental fence is required, do they have a preference on material type? | Chain link fence, with or without extenders, barbed wire, razor wire, will not be accepted; ornate is not preferred. Decorative iron, welded wire and other could be proposed. EPE is looking for creative, cost-effective fencing. In the pricing breakdown, please show fencing as a line item.
18 | What are the peak hours EPE would prefer the solar production shifted to? And what, if any, is the tiered or relative value in one set of hours versus another? | EPE's preference for production shifting is between 15:00 and 20:00. EPE would like to evaluate all options proposed by bidders not only solar shifting but also peak shaving and curve smoothing.
19 | Is there any chance El Paso Electric will be releasing CAD files corresponding to the Alta surveys you have provided? | CAD files are not available at this time.